| NR; DESCRIPTION; MODE; NR; DESCRIPTION; MODE. 1; DV-5A Deluge Valve; 10; Automatic drain valve. 2; Main shut off Valve; Normally open; 11; System drain valve; Normally closed. 3; Ball valve C1; Normally open; 12; Main drain valve; Normally closed. 4; Manual control station; Normally closed; 13; Pressure switch C3. 5; Solenoid valve C2; Normally closed; 14; Alarm test valve; Normally closed. 6; Gauge, upstream; 15; Strainer. 7; Gauge valve; Normally open; 16. 8; Gauge, pressure in diaphragm chamber; 17. 9; Manual reset actuator; 18. C1 – Diaphragm chamber, supply valve C2 – Solenoid valve, electrically controlled valve via actuating panel C3 – Pressure of the water flow. Diaphragm Cover Bolts Minimum Torque Nominal Valve Sizes, dimension. Torque N/m; DN40; DN50; DN80; DN100; DN150; DN200. Nuts; 59,7; 59,7; 254,9; 536,9; 359,3; 738,9. Short Hex Bolts; 47,5; 47,5; 203,4; 428,4; 287,4; 591,1. | DV-5A; Automatic Water Control Valve Deluge Fire Protection Systems Electric Actuation Trim. Function Model DV-5A is an electric actuated deluge valve which is typically activated by a fire alarm system. The detection of a fire through the fire panel will activate the DV-5A Deluge Valve. Draining the system after activation Important: Before operating any valve or activating any alarm, inform the local fire marshal and the alarm monitoring center. - Shut off the main pump (ULF PUMP in position 0) - Close the main shutoff valve ②. - Close the diaphragm supply valve ③ to the diaphragm chamber and the manual control station ④. - Open the drain valves ⑪⑫. Drain the entire system. Verify that the system is drained by pressing the automatic drain valve ⑩, no water should drain from the valve. Taking the system in operation - Close all the drain valves ⑪⑫. - Reset the fire panel in accordance with the manufacturer’s instructions in order to de-energies the solenoid valve ⑤. - Open the diaphragm supply valve ③. When the water flows from the tube, push the manual reset actuator ⑨. This pressurizes the diaphragm chamber, gauge ⑧. - Slowly open the main shutoff valve ②. Water supply pressure, gauge ⑧, rises to the set level. - Check that no water flows into the automatic drain valve ⑩. If no water runs out of the valve, the DV-5A Deluge valve is operative. - Turn the main pump to automatic (ULF PUMP in position AUTO) Alarm Test Important: Before operating any valve or activating any alarm, inform the local fire marshal and the alarm monitoring center. - Check that no water flows out of the automatic drain ⑩. - Open the alarm test valve ⑭ and check that the alarm triggered (red LED ‘gas released’). - Close the alarm test valve ⑭ and inform the local fire marshal and the alarm monitoring center that the test is completed. DATASHEET. |
| --- | --- |