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	 Order no. / Auftrags-Nr.
	 Consignment no. / Komm.-Nr.
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	 Remarks / Bemerkung

	 

	

	 Electrical data / Elektrische Daten
	Safe Area



	U
[V]
	Δ / Y
	f
[Hz]
	P
[kW]
	P
[hp]
	I
[A]
	n
[1/min]
	M
[Nm]
	η 3)
	cosφ 3)
	IA/IN
II/IN
	MA/MN
TI/TN
	MK/MN
TB/TN
	IE-CL

	
	
	
	
	
	
	
	
	4/4
	3/4
	2/4
	4/4
	3/4
	2/4
	
	
	
	

	DOL duty (S1) / Netzbetrieb (S1) - 155(F) to 130(B)

	230
	Δ
	50
	0.75
	-/-
	2.70
	2850
	2.5
	80.7
	82.2
	81.9
	0.86
	0.82
	0.73
	6.2
	2.6
	3.0
	IE3

	400
	Y
	50
	0.75
	-/-
	1.56
	2850
	2.5
	80.7
	82.2
	81.9
	0.86
	0.82
	0.73
	6.2
	2.6
	3.0
	IE3

	460
	Y
	60
	0.86
	-/-
	1.63
	3450
	2.4
	77.0
	78.0
	77.2
	0.86
	0.82
	0.73
	6.4
	2.6
	3.1
	IE3

	460
	Y
	60
	0.75
	-/-
	1.45
	3480
	2.0
	77.0
	77.2
	75.7
	0.84
	0.79
	0.70
	7.1
	3.0
	3.6
	IE3

	IM B3 / IM 1001
	
	FS 80 M
	
	IP55
	UKCA
	IEC/EN 60034
	IEC, DIN, ISO, VDE, EN
	 
	

	Environmental conditions / Umgebungsbedingungen :  -20 °C - +40 °C  /  1000 m
	Locked rotor time (hot / cold) / Festbremszeit (warm / kalt) : 21.2 s | 27.9 s



 Data sheet for three-phase Squirrel-Cage-Motors SIMOTICS
 Datenblatt für Drehstrom-Käfigläufermotoren

 Motor type /  Motor Typ : 1AV3082A				SIMOTICS GP - 80 M - IM B3 - 2p


	 Notes:

	IA/IN = locked rotor current / current nominal
MA/MN = locked rotor torque / torque nominal
	1) L10mh according to DIN ISO 281 10/2010
2) at rated power / at full load
	3) Value is  valid  only for DOL operation with motor design IC411

	MK/MN = break down torque / nominal torque
	

	responsible dep.
	technical reference
	created by
	approved by
	Technical data are subject to change! There may be discrepancies between calculated and rating plate values.
	

	DI MC LVM
	
	DT Configurator
	
	
	

	[image: \\FS01\Daten\LOGO ELEKTRA\Logo-Elektra-11.10.2018.JPG] 
	document type
	document status
	

	
	datasheet
	released
	

	
	title
	document number
	

	
	1TZ9003-0DA22-2AB4-Z
L20
	
	

	
	
	rev.
	creation date
	language
	Page

	
	
	924
	2023-05-19 11:27
	en/de
	1/2



	 Mechanical data / Mechanische Daten




	 Notes:
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	Sound level (SPL / SWL) at 50Hz|60Hz
Schallpegel (LpA / LwA) bei 50Hz|60Hz
	60 / 71 dB(A) 2) 3)
	64 / 75 dB(A) 2) 3)

	Moment of inertia
Trägheitsmoment
	0.0011 kg m²

	Bearing DE | NDE
Lager AS | BS
	6004 2Z C3
	6004 2Z C3

	bearing lifetime / Lagerlebensdauer

	L10mh FRad min for coupling operation 50|60Hz 1)
L10mh FRad min bei Kupplungsbetrieb  50|60Hz 1)
	40000 h
	32000 h

	Regreasing device
Nachschmiereinrichtung
	Without
ohne

	Grease nipple
Schmiernippel
	-/-

	Type of bearing
Art der Lagerung
	Locating bearing DE
Festlager DE (AS)

	Condensate drainage holes
Kondenswasserlöcher
	Without
Ohne

	External earthing terminal
Äußere Erdungsklemme
	Without
Ohne

	Vibration severity grade
Schwinggrößenstufe
	A
A

	Thermal class
Wärmeklasse
	F
F

	Duty type
Betriebsart  
	S1

	Direction of rotation
Drehrichtung
	bidirectional
bidirektional

	Frame material
Gehäusematerial
	aluminum
Aluminium

	Net weight of the motor (IM B3)
Nettogewicht des Motors (IM B3)
	11 kg

	Coating (paint finish)
Endanstrich
	Standard paint finish C2
Normalanstrich C2

	Color, paint shade
Farbe, Farbton
	RAL7030

	Motor protection
Motorschutz
	(B) 1 PTC thermistor - for tripping (2 terminals)
(B) 1 Kaltleiter PTC - für Abschaltung (2 Klemmen)

	Method of cooling
Kühlart
	IC411 - self ventilated, surface cooled
IC411 - Eigenbelüftet Oberflächengekühlt




	 Terminal box / Anschlusskasten



	[bookmark: _Hlk20906389]Terminal box position
Klemmenkastenlage
	top
oben

	Material of terminal box
Klemmenkastenmaterial
	Aluminium
Aluminium

	Type of terminal box
Klemmenkastentyp
	TB1 E00

	Contact screw thread
Gewinde Kontaktschraube
	M4

	Max. cross-sectional area
Max. Leiterquerschnitt
	1.5 mm2

	Cable diameter from ... to ...
Kabeldurchmesser von ... bis ...
	9 mm - 17 mm

	Cable entry
Kabeleinführung
	1xM25x1,5-1xM16x1,5

	Cable gland 
Kabelverschraubung
	2 plugs
2 Stopfen

	







	 Special design / Sonderausführung



	

	L20
	Locating bearing, DE 
Festlager DE (AS) 
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