PUMP TECHNICAL DATA SHEET

| Pump | TRMB 25-30/C/RZIE3 | KW 1.1 | Item A |
| --- | --- | --- | --- |
| PUMPED LIQUID |  |  |  |
| Pumped liquid | Air / Air |  |  |
| Temperature | 20 | °C |  |
| Specific gravity | 1 | kg/m³ |  |
| Viscosity |  | cP |  |
| OPERATING DATA |  |  |  |
| Flow rate | 11–28 | m³/h |  |
| Head |  | m.w.c. |  |
| NPSH R |  | m.w.c. |  |
| MOTOR |  |  |  |
| Installed power |  | kW |  |
| Absorbed power | 0.5–0.7 | kW |  |
| Speed | 2900 | RPM |  |
| VACUUM |  |  |  |
| Service liquid | Water |  |  |
| Temperature | 20 | °C |  |
| Port | 4–2 | L/min |  |
| Suction | 33–900 | mbar |  |
| Discharge | 1013 | mbar |  |
| PUMP DATA |  |  |  |
| Execution | Monoblock |  |  |
| ATEX | SAFE ZONE |  |  |
| Size | Single-stage liquid-ring vacuum pump |  |  |
| Construction | Mechanical seal: A Components – dimensions/designation according to ISO 3069 / UNI EN 12756 |  |  |
| Threaded ports | Ports: G 1 thread – according to UNI ISO 228-1 |  |  |
| Materials | Body: cast iron – Impeller: AISI 316 stainless steel – Shaft: AISI 420 stainless steel |  |  |
| Particulars | Construction: Direct monoblock coupling for IEC B34 motor with special shaft projection. Threaded connections according to UNI ISO 228-1. Coupled with electric motor supplied by us: efficiency class IE3; mounting form B34; frame size 80; power 0.85/1.1 kW; 2 poles / 50–60 Hz; voltage 230/400 – 0.85 kW – IE4; 460/440 – 1.1 kW 60 Hz – IE3; IEC Premium IE4 – 230/400 V – 1.1 kW 60 Hz – IE3; IEC 240/415 V – 0.85 kW 50 Hz – IE3; IEC Premium IE4 – 240/415 V – 0.85 kW 50 Hz – IE3. IE3 + service factor = 1.15. IP55 protection – Class F insulation with Class B temperature rise. Tropicalized – reinforced insulation for inverter operation. |  |  |
| API PLAN TYPE |  |  |  |
| API Plan | Seal flushing: API PLAN 01 – Internal fluid circulation. |  |  |
| SEALING SYSTEM |  |  |  |
| Mechanical seal type 1 | Ø22 TM SD 22 EN 12756 AQ1VGG – graphite / silicon carbide / Viton |  |  |
| Mechanical seal type 2 |  |  |  |
| ASSEMBLY |  |  |  |
| Configuration | Monoblock |  |  |
| ELECTRIC MOTOR DATA |  |  |  |
| Supplier | BONORA brand |  |  |
| Type | CVE |  |  |
| Efficiency class | IE3 |  |  |
| Mounting form | B34 |  |  |
| Poles / Frequency | 2 / 50–60 Hz |  |  |
| Unit size | IEC 80 |  |  |
| Motor standards | IEC |  |  |
| Frame | 56 |  |  |
| Shaft diameter | 9 |  |  |

Translated and transcribed from the provided technical sheet.